AR7091G Industrial Edge Computing Gateway User Manual

Water conservancy Video RTU/ Power Communication Management

Machine/Edge Computing Gateway /CPE

Xiamen Alotcer Communication Technology Co., Ltd.

Tel:+86-18106932752

Fax:+86 592-6195620

Web: https://www.alotceriot.com/

E-mail:anne@alotcer.com

Add: Room 502, No.146 Xinglinbei 2nd Road, Jimei District, Xiamen, China, 361022

- Applicable Models

| Product Type | Model | Product Name |
| --- | --- | --- |
| Standard | AR7091G-RS | 5G Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-LS | 5G Redcap Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-FS | 4G FDD Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-QS | 4G FDD/TDD Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-HS | 4G Cat1 Dual SIM Industrial Edge Computing Gateway |
| Standard+ GPS | AR7091G-RSP | GPS+5G Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-LSP | GPS+5G Redcap Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-FSP | GPS+4G FDD Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-QSP | GPS+4G FDD/TDD Dual SIM Industrial Edge Computing Gateway |
|  | AR7091G-HSP | GPS+4G Cat1 Dual SIM Industrial Edge Computing Gateway |
| Standard+ Dual Module | AR7091GS-RR | 5G Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-RF | 5G&4G Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-LL | 5G Redcap Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-FF | 4G FDD Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-HH | 4G Cat1 Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-HH | 4G Cat1 Dual Module Industrial Edge Computing Gateway |
| Standard+ GPS+ Dual Module | AR7091GS-RRP | GPS+5G Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-RFP | GPS+5G&4G Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-LLP | GPS+5G Redcap Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-FFP | GPS+4G FDD Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-QQP | GPS+4G FDD/TDD Dual Module Industrial Edge Computing Gateway |
|  | AR7091GS-HHP | GPS+4G Cat1 Dual Module Industrial Edge Computing Gateway |
| Enhanced | AR7091GK-RS | 5G Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-LS | 5G Redcap Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-FS | 4G FDD Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-QS | 4G FDD/TDD Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-HS | 4G Cat1 Dual SIM Enhanced Industrial Edge Computing Gateway |
| Enhanced+ GPS | AR7091GK-RSP | GPS+5G Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-LSP | GPS+5G Redcap Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-FSP | GPS+4G FDD Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-QSP | GPS+4G FDD/TDD Dual SIM Enhanced Industrial Edge Computing Gateway |
|  | AR7091GK-HSP | GPS+4G Cat1 Dual SIM Enhanced Industrial Edge Computing Gateway |
| Enhanced+ Dual Module | AR7091GKS-RR | 5G Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-RF | 5G&4G Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-LL | 5G Redcap Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-FF | 4G FDD Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-QQ | 4G FDD/TDD Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-HH | 4G Cat1 Dual Module Enhanced Industrial Edge Computing Gateway |
| Enhanced+ GPS+ Dual Module | AR7091GKS-RRP | GPS+5G Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-RFP | GPS+5G&4G Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-LLP | GPS+5G Redcap Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-FFP | GPS+4G FDD Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-QQP | GPS+4G FDD/TDD Dual Module Enhanced Industrial Edge Computing Gateway |
|  | AR7091GKS-HHP | GPS+4G Cat1 Dual Module Enhanced Industrial Edge Computing Gateway |

- Version

| Version | Author | Check | Date | Description |
| --- | --- | --- | --- | --- |
| V1.0 | Lanw | Deron | 2023-3-13 | Initial |
| V1.1 | Lanw | Deron | 2023-6-6 | 1,Update product models |
| V1.2 | Deron |  | 2024-7-26 | 2,Add 5G Redcap models |
| V1.3 | Deron |  | 2024-10-23 | 1,Add North&South End protocol |
| V1.4 | Deron |  | 2025-4-8 | 1,Add North protocol:ModbusRTU/TCP 2,Update the “Function Extension 2” description. |

- Contents

Applicable Models	2

Version	4

Contents	5

Chapter 1 Brief Introduction	6

1.1 General	6

1.2 Product Feature	6

1.3 Block Diagram	9

1.4 Product SPEC	9

1.5 Ordering Information	12

Chapter 2 Installation Introduction	14

2.1 General	14

2.2 Packing List	14

2.3 User Interface Description	14

2.4 Installation and Cable Connection	17

2.5 Power	22

2.6 LED	23

2.7 Reset Button Introduction	23

2.8 Installation Introduction	24

2.9 Lightning protection Introduction	24

- Brief Introduction

General

AR7091G is an industrial Internet of Things edge computing gateway /CPE/ water conservancy video RTU/ power communication management machine developed based on 5G/4G/3G/2G, WiFi, VPN technologies. The product adopts high-performance industrial 32-bit processor, with embedded operating system. It supports 1 Gigabit Ethernet WAN/1 Gigabit SFP optical port (optional), 4 Gigabit Ethernet LAN ports (PoE is optional for 2), 1 RS232 (2 for enhanced model), 4 isolated RS485 (7 for enhanced model), 1 USB2.0, 1 Micro SD card, 1 rainfall collection, 1 AI, 2 DI, 2 relay, 2 controllable power supplies, 1 CAN bus, 2.4G/5.8G WiFi interface that can conveniently connect one device to a cellular network. It can be connected to serial device, Ethernet device and WiFi device at the same time.

It has been widely used on M2M fields, such as intelligent transportation, smart grid, postal services, industrial automation, telemetry, finance, POS, water supply, environment protection, post, weather, and so on.

Application Topology

Product Feature

| Items | Contents |
| --- | --- |
| Industrial Design | High-powered industrial cellular module |
|  | High-powered industrial 32-bit CPU |
|  | Housing: iron, providing IP30 protection. |
|  | Power range: DC 9~35V |
| High Reliability | Support hardware and software WDT |
|  | Support auto recovery mechanism to make router always online |
|  | Ethernet port: 1.5KV magnetic isolation protection |
|  | RS232/RS485 port: 15KV ESD protection |
|  | SIM/UIM port: 15KV ESD protection |
|  | Power port: reverse-voltage and over voltage protection |
|  | Antenna port: lightning protection(optional) |
| Standard and Convenience | Support standard RS232(or RS485/RS422), Ethernet and WiFi port that can connect to serial, Ethernet and WiFi devices directly |
|  | Support standard WAN port and PPPOE protocol that can connect to ADSL directly |
|  | Support intellectual mode, enter into communication state automatically when powered |
|  | Support several work modes |
|  | Convenient configuration and maintenance interface（WEB or CLI） |
| High-performance and Security | Support multiple WAN access methods, including static IP, DHCP, PPPOE, 2.5G/3G/4G/5G. |
|  | Support double link backup between 2.5G/3G/4G/5G and WAN (optional). |
|  | Support VPN (PPTP, L2TP, IPSEC, Openvpn and GRE (TAP)) |
|  | Support remote management, SYSLOG, SNMP, TELNET, SSH, HTTPS, etc. |
|  | Support local and remote firmware upgrade, import and export configure file. |
|  | Support NTP, RTC embedded. |
|  | Support multiple DDNS provider service. |
|  | Support MAC address cloning. |
|  | WiFi support 802.11b/g/n/ac. support AP, client. |
|  | WiFi support 802.11ax (optional) |
|  | WiFi support WEP, WPA, WPA2 encryption. |
|  | Support multiple online trigger ways, including SMS, ring and data. Support link disconnection when timeout. |
|  | Support APN/VPDN. |
|  | Support VRRP link backup |
|  | Support multiple DHCP server and DHCP client, DHCP binding MAC address, DDNS, Firewall, NAT, DMZ host, QoS, traffic statistics, real-time display data transfer rate etc. |
|  | Support IoT protocol MQTT client and server (support CA) |
|  | Support industrial control OPCUA protocol and MODBUS protocol conversion |
|  | Support Python secondary development platform (Python3) |
|  | Support TCP/IP, UDP, FTP(optional), HTTP, etc. |
|  | Supports SPI firewall, VPN pass-through, access control, URL filtering,etc. |
|  | Support local log storage. |
|  | Support GPS(optional). |
|  | Support dual 4G/5G module (optional) |
|  | Support PoE (optional) |
|  | Support SFP (optional) |
|  | Support online network testing |
|  | Support rainfall data collection (enhanced model) |
|  | Support CAN bus communication (enhanced model) |
|  | Support analog data collection (enhanced model) |
|  | Support digital data collection (enhanced model) |
|  | Support the photo capture function |
|  | Support NB-IoT, Lora, Ultrashort wave communication |
|  | The modular architecture of hardware and software |
|  | Support customization of I/O interfaces board |
| North End protocol - Report | MQTT (JSON)/Mobile cloud/Alibaba Cloud/Telecom cloud/Huawei Cloud |
|  | ModbusRTU/TCP |
|  | OPCUA (Optional) |
|  | IEC101 (Optional) |
|  | IEC104 (Optional) |
| South End Protocol - Acquisition | ModbusRTU/TCP/OverTCP |
|  | Siemens S7-S200/S200Smart/S300/S400/S1200/S1500 (Optional) |
|  | DLT645 (Optional) |
|  | DNP3.0 Master (Optional) |

Block Diagram

Product SPEC

| Items |  | Contents |
| --- | --- | --- |
| Hardware System | CPU | Industrial 32-bit CPU |
|  | FLASH | 16MB (Extendable to 64MB) |
|  | SDRAM | 512MB |
| Interface | WAN | 1 Gigabit WAN port(RJ45) /1 Gigabit SFP optical port (optional, the Ethernet and SFP cannot be used at the same time), auto MDI/MDIX, 1.5KV magnetic isolation protection |
|  | LAN | 4 Gigabit Ethernet ports(RJ45), auto MDI/MDIX, 1.5KV magnetic isolation protection |
|  | Serial | 1 RS232 port (Shared with RS485, 2 for enhanced model), 4 isolated RS485 port( 7 for enhanced model, the RS232-0 and RS485-0 cannot be used at the same time, the RS232-1 and RS485-4 cannot be used at the same time),15KV ESD protection Data bits: 5, 6 ,7, 8 Stop bits: 1, 1.5(optional), 2 Parity: none, even, odd, space(optional), mark(optional) Baud rate: 2400~115200 bps |
|  | Antenna | Cellular: Standard SMA female interface, 50 ohm WiFi: Standard SMA male interface, 50 ohm GPS(optional):Standard SMA female interface, 50 ohm |
|  | SIM/UIM | Standard 3V/1.8V user card interface, 15KV ESD protection |
|  | Micro SD card | Standard self-propelled Micro SD card interface (Max 128GB) |
|  | USB | Standard USB2.0 Type-A, support USB storage |
|  | Power | Standard 2-PIN 3.81mm terminal, reverse-voltage and over voltage protection |
|  | Reset | Press this key for 8 seconds to restore the module to its original factory default settings |
|  | Extended application interface (enhanced model) | 1 rainfall collection |
|  |  | 2 analog input ports, 12-bit ADC, support 4-20mA or 0-5V, accuracy: 0.5% |
|  |  | 2 optical isolation digital input ports Logic 0: wet contact 0-3V DC, or dry contact is connected Logic 1: wet contact 5-30V DC, or dry contact is disconnected |
|  |  | 1 CAN bus (compatible with ISO 11898 standard) |
|  |  | 2 relay interfaces Maximum switching voltage: 30V DC/250V AC Maximum switching current: 5A Maximum switching power: 150W |
|  |  | 2 controllable power supplies (The output voltage is equal to the power supply voltage of the device. The default value is 12V DC. Single rated output current 1A, total rated output current 2A, built-in overcurrent protection, enhanced model) |
|  | LED | “PWR”, “RUN”, “SIM1”, “SIM2”, “Online”, “LAN1”, “LAN2”, “LAN3”, “LAN4”, “WAN”, “MOD1 Signal strength”, “MOD2 Signal strength”, “WiFi2.4”, “WiFi5.8” |
| Network | Wireless Network | 5G NR SA/NSA:n1/2/3/5/7/8/12/20/28/41/66/71/ 77/78/79 TDD-LTE:B38/39/40/41 FDD-LTE:B1/2/3/4/5/7/8/13/17/20/25/28 WCDMA:850/900/1900/2100MHz TD-SCDMA:1880-1920/2010-2025MHz(A/F) CDMA2000 1x/ EVDO Rev. A:800/1900MHz GSM/GPRS/EDGE:850/900/1800/1900MHz CDMA:800/1900MHz |
|  | WAN | Support PPP/PPPOE |
|  | LAN | Support APR |
|  | Network Authentication | Support CHAP/PAP Authentication |
|  | Network Access | Support APN/VPDN |
|  | IP Applications | Support Ping、Trace、DHCPServer 、DHCP Relay、 DHCP Client、DNS relay、DDNS 、Telnet |
|  | IP Routing | Support static routing |
| WiFi | Standard | IEEE802.11b/g/n, 2.4G support AP and Station mode IEEE802.11ac, 5.8G support AP and Station mode IEEE802.11ax, 2.4G & 5.8G (optional) |
|  | Bandwidth | IEEE802.11b/g: 54Mbps (max) IEEE802.11n: 300Mbps (max) IEEE802.11ac: 866Mbps (max) IEEE802.11ax: 1201Mbps (max) |
|  | Security | WEP, WPA, WPA2, etc. WPS (optional) |
| GPS (optional) | Receiver Type | 50-channle GPS L1(1575.42MHz) C/A code SBAS: WAAS,EGNOS,MSAS,GAGAN |
|  | Max. update rate | 5 Hz |
|  | Accuracy | Position: 2.5m CPE SBAS: 2.0m CPE |
|  | Location | Cold starts: 32s Warm starts: 32s Aided starts: <1s Hot starts: <3s |
|  | Sensitivity | Tracking: -160dBm Reacquisition: -160dBm Cold starts: -146dBm |
|  | Timing accuracy | RMS: 30ns 99%: <60ns Granularity: 21ns |
|  | Time pulse | Configurable, 0.25 to 1000Hz |
| Power supply (standard model) | Power range | DC 9~35V (12V DC recommended) |
|  | Consumption1 | <660mA (@12V DC, one module 4G) |
|  | Consumption2 | <680mA (@12V DC, dual module 4G) |
|  | Max current | <1200mA (@12V DC, dual 5G) |
| Power supply (enhanced model) | Power range | DC 9~35V (12V DC recommended) |
|  | Consumption1 | <700mA (@12V DC, one module 4G) |
|  | Consumption2 | <740mA (@12V DC, dual module 4G) |
|  | Max current | <1200mA (@12V DC, dual 5G) |
| Mechanical | Dimensions | 209x150x55mm (excluding accessories) |
|  | Weight | 1575g (excluding accessories) |
| Environmental Limits | Operating Temperature | -35~+75ºC (-31~+167℉) |
|  | Storage Temperature | -40~+85ºC (-40~+185℉) |
|  | Operating Humidity | - 95% (Non-condensing) |
| Installation | Hanger | The fixing piece is at both sides |
|  | Rail | 35mm DIN rail |

Ordering Information

| Model | Version |  |  |
| --- | --- | --- | --- |
|  | Network Abbreviation | Function Extension 1 | Function Extension 2 |
| AR7091G (Standard) | -R: 5G -L: 5G Redcap -F: 4G FDD-LTE -Q: 4G FDD/FDD-LTE -H: 4G Cat1 -N: Without wireless Module | S: Dual SIM Card P: GPS | E: Encryption F: Optical fiber Q: PoE B: Bluetooth L: Lora |
| AR7091GS (Standard + Dual Module) | RR: Dual 5G LL: Dual 5G Redcap FF: Dual 4G FDD-LTE QQ: Dual 4G TDD/FDD-LTE HH: Dual 4G Cat1 RF: 5G+4G | P: GPS | E: Encryption F: Optical fiber Q: PoE B: Bluetooth L: Lora |
| AR7091GK (Enhanced) | -R: 5G -L: 5G Redcap -F: 4G FDD-LTE -Q: 4G FDD/FDD-LTE -H: 4G Cat1 -N: Without wireless Module | S: Dual SIM Card P: GPS | E: Encryption F: Optical fiber Q: PoE B: Bluetooth L: Lora |
| AR7091GKS (Enhanced + Dual Module) | RR: Dual 5G LL: Dual 5G Redcap FF: Dual 4G FDD-LTE QQ: Dual 4G TDD/FDD-LTE HH: Dual 4G Cat1 RF: 5G+4G | P: GPS | E: Encryption F: Optical fiber Q: PoE B: Bluetooth L: Lora |
| Example | 1. AR7091G-RSP：AR7091G 5G Standard Industrial Edge Computing Gateway/CPE, support GPS, Dual SIM Card. 2、AR7091GKS-RFP：AR7091GKS 5G+4G Enhanced Industrial Edge Computing Gateway/CPE, MOD 1 is 5G, MOD 2 is 4G, support GPS, Dual SIM Card, support extended application interface . |  |  |

- Installation Introduction

  - General

The edge computing gateway must be installed correctly to make it work properly.

Warning: Forbid to install the edge computing gateway when powered!

Packing List

| Name | Quantity | Remark |
| --- | --- | --- |
| Edge Computing Gateway host | 1 |  |
| Cellular antenna (Male SMA) | 2-6 |  |
| WiFi antenna (Female SMA) | 2-4 |  |
| SIM card holder | 2 |  |
| RJ45 network cable | 1 |  |
| Certification card | 1 |  |
| RS232 cable | 1 |  |
| 2pin 3.81mm pitch terminal (male) | 1 |  |
| 12pin 3.5mm pitch terminal (male) | 1-4 |  |
| 8pin 3.5mm pitch terminal (male) | 2 | Only enhanced model |
| Power adapter | 1 | Optional |
| Micro-SD card | 1 | Optional |
| RS485 cable | 1 | Optional |
| GPS antenna | 1 | Optional |

User Interface Description

User Interface Definition Table

| Number | Function | Name | Default | Remark |
| --- | --- | --- | --- | --- |
| 1-1 | 232-0 | RX0 | Channel 0 RS232 receiver (Edge Computing Gateway receiver) | The RS232-0 and RS485-0 cannot be used at the same time |
| 1-2 |  | TX0 | Channel 0 RS232 transmitter (Edge Computing Gateway transmitter) |  |
| 1-3 |  | GND | Channel 0 RS232 GND |  |
| 1-4 | 485-0 | A0 | Channel 0 RS485 A |  |
| 1-5 |  | B0 | Channel 0 RS485 B |  |
| 1-6 | 485-1 | A1 | Channel 1 RS485 A |  |
| 1-7 |  | B1 | Channel 1 RS485 B |  |
| 1-8 | 485-2 | A2 | Channel 2 RS485 A |  |
| 1-9 |  | B2 | Channel 2 RS485 B |  |
| 1-10 | 485-3 | A3 | Channel 3 RS485 A |  |
| 1-11 |  | B3 | Channel 3 RS485 B |  |
| 1-12 | NA | NC | Not Connected |  |
| 2-1 | CAN Bus | CANL | Low level CAN bus line | Compatible with ISO 11898 standard |
| 2-2 |  | CANH | High level CAN bus line |  |
| 2-3 | 232-1 | GND | Channel 1 RS232 GND | The RS232-1 and RS485-4 cannot be used at the same time |
| 2-4 |  | RX1 | Channel 1 RS232 receiver (Edge Computing Gateway receiver) |  |
| 2-5 |  | TX1 | Channel 1 RS232 transmitter (Edge Computing Gateway transmitter) |  |
| 2-6 |  | GND | Channel 1 RS232 GND |  |
| 2-7 | 485-4 | A4 | Channel 4 RS485 A |  |
| 2-8 |  | B4 | Channel 4 RS485 B |  |
| 2-9 | 485-5 | A4 | Channel 5 RS485 A |  |
| 2-10 |  | B4 | Channel 5 RS485 B |  |
| 2-11 | 485-6 | A4 | Channel 6 RS485 A |  |
| 2-12 |  | B4 | Channel 6 RS485 B |  |
| 3-1 | Analog Input | ADC0 | Channel 0 analog input | 12-bit ADC, support 4-20mA or 0-5V, accuracy: 0.5% |
| 3-2 |  | AGND | Analog GND |  |
| 3-3 |  | ADC1 | Channel 1 analog input |  |
| 3-4 | Digital input | DIN0 | Channel 0 digital input | Optical isolation Logic 0: wet contact 0-3V DC, or dry contact is connected Logic 1: wet contact 5-30V DC, or dry contact is disconnected |
| 3-5 |  | DGND | Digital GND |  |
| 3-6 |  | DIN1 | Channel 1 digital input |  |
| 3-7 | Rainfall | GND | Udometer GND | Udometer interface |
| 3-8 |  | Rain | Udometer input |  |
| 4-1 | Relay-0 | K0+ | Channel 0 relay positive | Maximum switching voltage: 30V DC/250V AC Maximum switching current: 5A Maximum switching power: 150W |
| 4-2 |  | K0- | Channel 0 relay negative |  |
| 4-3 | Relay-1 | K1+ | Channel 1 relay positive |  |
| 4-4 |  | K1- | Channel 1 relay negative |  |
| 4-5 | Vout-0 | V0- | Channel 0 controllable power output negative | The output voltage is equal to the power supply voltage of the device The default value is 12V DC Single rated output current 1A |
| 4-6 |  | V0+ | Channel 0 controllable power output positive |  |
| 4-7 | Vout-1 | V1- | Channel 1 controllable power output negative |  |
| 4-8 |  | V1+ | Channel 1 controllable power output positive |  |
| 5-1 | NA | NC | Not Connected | Customizable function |
| 5-2 | NA | NC | Not Connected | Customizable function |
| 5-3 | NA | NC | Not Connected | Customizable function |
| 5-4 | NA | NC | Not Connected | Customizable function |
| 5-5 | NA | NC | Not Connected | Customizable function |
| 5-6 | NA | NC | Not Connected | Customizable function |
| 5-7 | NA | NC | Not Connected | Customizable function |
| 5-8 | NA | NC | Not Connected | Customizable function |
| 5-9 | NA | NC | Not Connected | Customizable function |
| 5-10 | NA | NC | Not Connected | Customizable function |
| 5-11 | NA | NC | Not Connected | Customizable function |
| 5-12 | NA | NC | Not Connected | Customizable function |
| 6-1 | NA | NC | Not Connected | Customizable function |
| 6-2 | NA | NC | Not Connected | Customizable function |
| 6-3 | NA | NC | Not Connected | Customizable function |
| 6-4 | NA | NC | Not Connected | Customizable function |
| 6-5 | NA | NC | Not Connected | Customizable function |
| 6-6 | NA | NC | Not Connected | Customizable function |
| 6-7 | NA | NC | Not Connected | Customizable function |
| 6-8 | NA | NC | Not Connected | Customizable function |
| 6-9 | NA | NC | Not Connected | Customizable function |
| 6-10 | NA | NC | Not Connected | Customizable function |
| 6-11 | NA | NC | Not Connected | Customizable function |
| 6-12 | NA | NC | Not Connected | Customizable function |

Installation and Cable Connection

Dimension (The fixing piece is detachable): (Unit: mm)

Installation of antenna:

Cellular antenna (Standard)   WiFi antenna (Standard)    GPS antenna (Optional)

Antenna installation

Screw the SMA male pin of the cellular antenna to the female SMA interface of the edge computing gateway with sign “5G/4G” (some models are 2-6 antennas, namely "ANT1-ANT4", "ANT11, ANT12").

Screw the SMA female pin of the WiFi antenna to the male SMA interface of the edge computing gateway with sign “WiFi” (some models are 2-4 antennas, namely "ANT5-ANT8").

Screw the SMA male pin of the GPS antenna (optional) to the female SMA interface of the edge computing gateway with sign “GPS” (namely "ANT10).

Warning: The cellular antenna and the WiFi antenna cannot be connected wrongly. And the antennas must be screwed tightly, or the signal quality of antenna will be influenced!

Installation of SIM/UIM card:

SIM/UIM Card Installation

Firstly power off the edge computing gateway, and press the out button of the SIM/UIM card outlet with a needle object. Then the SIM/UIM card sheath will flick out at once. Put SIM/UIM card into the card sheath (Pay attention to put the side which has metal point outside), and insert card sheath back to the SIM/UIM card outlet.

Warning: Forbid to install SIM/UIM card when powered!

Installation of cable:

Edge computing gateway uses the industrial terminal interface. It is recommended to use 22-16 AWG cables for power supply and 28-18 AWG cables for communication

| RS232 cable (standard) | RJ45 network cable (standard) |
| --- | --- |
| Power adapter (optional) | RS485 cable (optional) |

RS232 cable:

The signal definition of the DB9F serial communication interface is as follows:

| Color of wire | DB9 female |
| --- | --- |
| Blue(TX) | 2 |
| Brown(RX) | 3 |
| Black(GND) | 5 |

Debug cable:

Debug Serial port is the same serial port as RS232-0. The connection is refer to the figure above (RS232 cable).

Power adapter:

The definition of the 2pin industrial terminal (3.81mm pitch) is as follows:

| Number | Definition | Remark |
| --- | --- | --- |
| 1 | V+ | Power positive |
| 2 | V- | Power negative |

Network cable:

Insert one end of the network cable into the switch interface with sign “LAN1/LAN2/LAN3/LAN4”, and insert the other end into the Ethernet interface of user’s device. The signal connection of network direct cable is as follows:

| RJ45-1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RJ45-2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

RS485 cable:

The signal definition of the RS485 serial communication interface is as follows:

| Color of wire | Definition |
| --- | --- |
| Red | RS485 A |
| Black | RS485 B |

Digital input: (Dry contact, logic 0: connected, logic 1: disconnected)

(Wet contact, logic 0: 0-3V DC, logic 1: 5-30V DC)

Relay: (Maximum switching voltage: 30V DC/250V AC, Maximum switching current: 5A, Maximum switching power: 150W)

Controllable power output: (The output voltage is equal to the power supply voltage of the device. The default value is 12V DC. Single rated output current 1A, total rated output current 2A, built-in overcurrent protection, enhanced model)

Analog input: (12-bit ADC, Input current range: 4-20mA, input voltage range: 0-5V)

Udometer：

CAN Bus: (Meets ISO 11898)

Power

Power Adapter (optional)

The power range of the edge computing gateway is DC 9~35V.

Warning: When we use other power, we should make sure that the power can supply power above 15W.

We recommend user to use the optional DC 12V/1.5A power.

LED

The edge computing gateway provides following LED lights: “PWR”, “RUN”, “SIM1”, “SIM2”, “Online”, “LAN1”, “LAN2”, “LAN3”, “LAN4”, “WAN”,  “MOD1 Signal strength”, “MOD2 Signal strength”, “WiFi2.4”, “WiFi5.8”

| LED | State | Description |
| --- | --- | --- |
| MOD1/MOD2 Signal strength (Blue) | Off | The signal is terrible |
|  | Slow blink | Signal strength is weak |
|  | Fast blink | Signal strength is medium |
|  | Always on | Signal strength is good |
| Power(Red) | On | Device is powered on |
|  | Off | Device is powered off |
| RUN(Blue) | Blink | Device works normally |
|  | On/Off | Device does not work |
| SIM1(Blue) | On | SIM1/UIM1 card is recognized |
|  | Off | SIM1/UIM1 card is not recognized |
| SIM2(Blue) | On | SIM2/UIM2 card is recognized |
|  | Off | SIM2/UIM2 card is not recognized |
| Online(Green) | On | Device has logged on network |
|  | Off | Device hasn’t logged on network |
| LAN1(Yellow) | On/Blink | LAN1 is connected /Communicating |
|  | Off | LAN1 is not connected |
| LAN2(Yellow) | On/Blink | LAN2 is connected /Communicating |
|  | Off | LAN2 is not connected |
| LAN3(Yellow) | On/Blink | LAN3 is connected /Communicating |
|  | Off | LAN3 is not connected |
| LAN4(Yellow) | On/Blink | LAN4 is connected /Communicating |
|  | Off | LAN4 is not connected |
| WAN(Yellow) | On/Blink | WAN is connected /Communicating |
|  | Off | WAN is not connected |
| WiFi 2.4(Blue) | On | 2.4G WiFi is enable |
|  | Off | 2.4G WiFi is not enable |
| WiFi 5.8(Blue) | On | 5.8G WiFi is enable |
|  | Off | 5.8G WiFi is not enable |

Reset Button Introduction

The edge computing gateway has a “Reset” button to restore it to its original factory default settings. When user press the “Reset” button for up to 8 seconds, the edge computing gateway will restore to its original factory default settings and restart automatically. (The auto-restart is as follows: the "RUN" LED turns off for about 10 seconds and then functions are normally)

Installation Introduction

The enclosure supports mounting lug and 35mm DIN rail.

Lightning protection Introduction

We suggest to take some lightning protection measures (such as installing lightning protection device) to improve the safety protection level of the edge computing gateway when it is connected to an outdoor sensor, such as an udometer, etc.