AltRTU600L Industrial Cellular RTU User Manual

Support 5G/4G Industrial Data Acquisition instrument

Xiamen Alotcer Communication Technology Co., Ltd.

Tel:+86-18106932752

Fax:+86 592-6195620

Web: https://www.alotceriot.com/

E-mail:anne@alotcer.com

Add: Room 502, No.146 Xinglinbei 2nd Road, Jimei District, Xiamen, China, 361022

Applicable Models:

| Product Type | Model | Product Name |
| --- | --- | --- |
| Standard | AltRTU600L-R | 5G industrial cellular RTU |
|  | AltRTU600L-L | 5G Redcap industrial cellular RTU |
|  | AltRTU600L-A | 4G industrial cellular RTU |
|  | AltRTU600L-F | 4G FDD industrial cellular RTU |
|  | AltRTU600L-Q | 4G FDD/TDD industrial cellular RTU |
|  | AltRTU600L-H | 4G Cat1 industrial cellular RTU |
| GPS | AltRTU600L-RP | GPS+5G industrial cellular RTU |
|  | AltRTU600L-LP | GPS+5G Redcap industrial cellular RTU |
|  | AltRTU600L-AP | GPS+4G industrial cellular RTU |
|  | AltRTU600L-FP | GPS+4G FDD industrial cellular RTU |
|  | AltRTU600L-QP | GPS+4G FDD/TDD industrial cellular RTU |
|  | AltRTU600L-HP | GPS+4G Cat1 industrial cellular RTU |

- Version

| Version | Author | Check | Date | Description |
| --- | --- | --- | --- | --- |
| V1.0 | Hewenfeng | Deron | 2023-10-12 | Initial |

- Contents

Version	3

Contents	4

Chapter 1 Brief Introduction	5

1.1 General	5

1.2 Product Feature	5

1.3 Block Diagram	7

1.4 Product SPEC	8

1.5 Ordering Information	10

Chapter 2 Installation Introduction	11

2.1 General	11

2.2 Packing List	11

2.3 User Interface Description	12

2.4 Installation and Cable Connection	14

2.4.1 Installation of antenna:	14

2.4.2 Installation of SIM/UIM card:	15

2.4.3 Installation of cable:	15

2.5 Power Supply	19

2.6 Indicator Lights Introduction	19

2.7 Wake Up Button Description	20

2.8 Installation Instruction	20

2.9 Lightning protection Introduction	20

- Brief Introduction

General

AltRTU600L is an industrial cellular RTU developed based on 5G/4G LTE connectivity. It adopts high-powered industrial 32 bits CPU and industrial wireless module, and embedded real time operating system to realize comprehensive functions such as data acquisition, storage, control, alarm, remote transmission and remote management.

AltRTU600L supports RS232, RS485, Ethernet, Tipping bucket Rain gauge, Analog Input, Digital Input (dry and wet contacts), Digital Output, Relay Output and other interfaces. It supports internal flash and external expansion Micro-SD card to store data, and network communication through 5G or 4G, NB IoT, Lora, Ultra-short wave and other ways. It has powerful functions, stable performance, and supports low power consumption working mode.

AltRTU600L has been widely used in flood mitigation, hydrology, water resources, water pollution, environmental monitoring, meteorological monitoring, and so on.

Application Topology

Product Feature

| Items | Contents |
| --- | --- |
| Industrial Design | High-powered industrial cellular module |
|  | High-powered industrial 32bits CPU |
|  | Wide Operating Temperature(-35~+75ºC) |
|  | Power range: DC 9~35V |
| High Reliability | Support hardware and software WDT |
|  | Support auto recovery mechanism, including online detect, auto redial when offline to make it always online |
|  | Ethernet port: 1.5KV magnetic isolation protection |
|  | RS232/RS485ports:15KV ESD protection |
|  | SIM/UIM port: 15KV ESD protection |
|  | Strong anti-interference ability, suitable for various complex electromagnetic environments |
|  | Large data storage space(16MB), can store data more than 10 years |
|  | Power port: reverse-voltage and overvoltage protection |
|  | Antenna port: lightning protection(optional) |
| Standard and Convenience | Support standard RS232/RS485 and Ethernet ports that can connect to serial and network devices directly |
|  | Multiple low-power working modes to use Convenient and flexible |
|  | Multiple indicator lights that can indicate various system states |
|  | Supports serial port upgrade, remote maintenance, and device log export |
| Major Function | Trigger collection Rainfall data |
|  | Regularly collection Water Level, Rainfall , Water Quality, and other data |
|  | Regularly upload Rainfall, Water Level, Flow rate, Water Quality, and other data |
|  | Alarm trigger and upload Rainfall, Water Level, Flow rate, Water Quality, and other data |
|  | Local storage Rainfall, Water Level, Flow rate, Water Quality, and other data |
|  | Remote measurement current Rainfall, Water Level, Flow rate, Water Quality, and other data |
|  | Remote query local historical data |
|  | Local export historical data |
|  | Support upload battery voltage |
|  | Support capture image |
|  | Support local manual setting data |
|  | Backup data through 5G/4G network data communication and SMS |
|  | Support Communication Methods includes NB-IoT,Lora, Ultra-short wave,and so on |
|  | Built in temperature and humidity sensors |
|  | Support PoE(PSE)(optional) |
|  | Support GPS positioning (optional) |
| Protocol (Customizable) | SLT 180-2015 Hydrological Automatic Measurement and Reporting System Equipment Telemetry Terminal |
|  | SLT 102-1995 Basic technical conditions of Hydrological Automatic Measurement and Reporting System Equipment |
|  | SL61-2003 Technical Specification for Hydrological Automatic Measurement and Reporting System |
|  | SZY203-2016 Technical requirements for water resource monitoring equipment |
|  | SZY205-2016 Quality inspection of water resource monitoring equipment |
|  | GB 3096-2008 Acoustic Environmental Quality Standards |
|  | GB/T 16706-1996 Environmental pollution source category code |
|  | GB/T 19582-2008 Industrial Automation Network Specification Based on Modbus Protocol |
|  | HJ/T 75-2007 Technical Specification for Continuous Monitoring of Smoke Emissions from Fixed Pollution Sources (Trial) |
|  | HJ/T 76-2007 Technical requirements and monitoring methods for continuous monitoring of flue gas emissions from fixed pollution sources (Trial) |
|  | HJ 524-2009 Air pollutant name code |
|  | Data transmission standard for online monitoring (monitoring) system of pollutants |
|  | HJ/T212-2005 Data transmission standard for online automatic monitoring (monitoring) system of pollution sources |
|  | HJ 212-2017 Data transmission standard for online monitoring (monitoring) system of pollutants |
|  | HJ 477-2009 Technical requirements for online automatic monitoring (monitoring) data acquisition and transmission equipment for pollution sources |
|  | Communication protocol for hydrological monitoring data |
|  | Water resource monitoring data transmission protocol |

Block Diagram

Product SPEC

| Items |  | Contents |
| --- | --- | --- |
| Hardware System | CPU | Industrial 32bits CPU |
|  | FLASH | 512KB |
|  | SDRAM | 256KB |
|  | Data Flash | 16MB |
|  | Micro-SD Card | Support External Micro-SD Card |
| Interface | Serial Ports | 4 RS232 and 4 RS485 (RS232-0 and RS485-0 cannot be used simultaneously, RS232-1 and RS485-1 cannot be used simultaneously), built-in 15KV ESD protection. The serial port parameters are as follows: Data bits: 5, 6, 7, 8 Stop bits: 1, 1.5 (optional), 2 bits Verification: No verification, even verification, odd verification Serial port speed: 300~230400bps, default 115200bps Form: 3.5mm spacing industrial terminal |
|  | Debug Serial | 1 RS232 Debug serial port (common with RS485-3 ,switched through Debug switch). Form: standard DB9 female |
|  | Debug switch | Universal toggle switch |
|  | Ethernet | One 10/100M Ethernet port,Adaptive MDI/MDIX with built-in 1.5KV electromagnetic isolation protection. (PSE (optional), the equipment power supply voltage is required to meet 10.5~14VDC) |
|  | Antenna | Standard SMA female interface, 50 ohm |
|  | SIM/UIM | Standard drawer type user card interface，Support 1.8V/3V SIM/UIM card with built-in 15KV ESD protection |
|  | Micro-SD Card | Standard self-propelled Micro-SD card interface (Max 128GB) |
|  | Power | 1 main power supply, built-in power reverse protection and overcurrent and overvoltage protection,form: 2PIN 3.81MM pitch industrial terminal |
|  | Wake up button | Tact switch |
|  | Grounding terminal | M3 screw grounding protection terminal |
|  | User interface | 1 udometer interface |
|  |  | 4-channels analog input interface(12 bit ADC ,support 4-20mA or 0-5V, acquisition accuracy: 1-5V or 4-20mA accuracy within 0.5%, 0-1V accuracy within 5%) |
|  |  | 4-channels digital input interface (optical isolation) Logic 0: Wet node 0-3VDC, or dry node connect Logic 1: Wet node 5-30VDC, or dry node disconnect |
|  |  | 1-channels digital output interface (optical isolation, OC gate output) Rated driving current: 50mA Rated driving voltage: 35V |
|  |  | 2-channels relay output interface Maximum switching voltage: 30VDC/250VAC Maximum switching current: 5A Maximum switching power: 150W/1200VA |
|  |  | 4-channels controllable output power supply (output voltage value is the same as the supply voltage, default 12VDC. Single channel rated output current 1A, 4-channels rated output current total 2A, built-in overcurrent protection |
|  | Indicator lights | Power, Online, SIM, Run,APP,LINK |
| Network parameters | Wireless network | 5G NR SA/NSA: n1/2/3/5/7/8/12/20/28/41/66/ 71/77/78/79 TDD-LTE: B38/39/40/41 FDD-LTE: B1/2/3/4/5/7/8/13/17/20/25/28 WCDMA: 850/900/1900/2100MHz TD-SCDMA: 1880-1920/2010-2025MHz(A/F) CDMA2000 1x/ EVDO Rev. A: 800/1900MHz GSM/GPRS/EDGE: 850/900/1800/1900MHz CDMA: 800/1900MHz |
|  | NB-IoT Parameters | Frequency band: B5: 850MHz/B8: 900MHz/B20: 800MHz Theoretical bandwidth: 100bps~100Kbps Transmission power: 23 ± 1dBm Receiving sensitivity:<-129dBm |
|  | Lora Parameters | Frequency band:410MHz-441MHz,1000KHz step,recommended 433 ± 5MHz Indoor/urban communication distance: 1KM Outdoor/line of sight communication distance: 3KM Transmission power: 100mW Receiving sensitivity: ＜-140dBm |
| Installation mode | Fixed piece | Fixed with hanging ears on both sides |
|  | Rail | 35mm Din rail |
| Power Consumption | Power range | DC 9~35V (12V DC recommended) |
|  | Communication | <100mA (@12VDC) (only connected one RS485 sensor , and then communicates remotely with the data central for 100B/S.High power mode.) |
|  | Collection | <10mA (@12VDC) (only connected one RS485 sensor, RTU not online) |
|  | Sleep(Static duty) | <2mA (@12VDC) |
|  | Deep Sleep | < 40uA @ 12VDC |
| Physical | Dimensions | 116.2x114.2x33.1mm(Excluding accessories) |
|  | Shell | Metal shell, protection level IP30. Shell and system safety isolation, especially suitable for industrial control on-site applications |
|  | Weight | Approximately 460g |
| Environmental Limits | Operating Temperature | -35~+75ºC (-31~+167℉) |
|  | Storage Temperature | -40~+85ºC (-40~+185℉) |
|  | Operating Humidity | 95% (non-condensing) |

Ordering Information

| Model | Version |  |
| --- | --- | --- |
|  | Network Abbreviation | Function Extension |
| AltRTU600L | -R: 5G -L: 5G Redcap -A: 4G -F: 4G FDD -Q: 4G FDD/TDD -H: 4G Cat1 | S: Dual SIM P: GPS |
| Example | AltRTU600L-FP: 4G FDD industrial cellular RTU,support GPS. |  |

- Installation Introduction

  - General

The RTU must be installed correctly to achieve the designed function. It is recommended to install and debug the equipment under the guidance of qualified engineers recognized by our company.

Warning:

Forbid to install when powered!

Forbid to disassemble the device without permission.

Packing List

Please take good care of the packaging materials when unpacking the equipment without permission, so that they can be used for future transportation. The list is as follows:

| Name | Quantity | Remark |
| --- | --- | --- |
| AltRTU600L Host | 1 | standard |
| Cellular antenna | 1-3 | standard |
| SIM card holder | 1 | standard |
| RS232 cable | 1 | standard |
| Certification card | 1 | standard |
| Power adapter | 1 | optional |
| Debug serial cable | 1 | optional |
| Micro-SD card | 1 | optional |
| GPS antenna | 1 | optional |
| RS485 cable | 1 | optional |
| RJ45 network cable | 1 | optional |

User Interface Description

Interface definition:

| Number | Function | Name | Default | Remark |
| --- | --- | --- | --- | --- |
| 1-1 | ADC Input | AI0 | Channel 0 analog input | 12 bit ADC (support 4-20mA or 0-5V, acquisition accuracy: 1-5V or 4-20mA accuracy within 0.5%, 0-1V accuracy within 5%) Output voltage is equal to the power supply voltage (default 12V) ,Single rated output current 1A |
| 1-2 |  | V0+ | Channel 0 controllable power output positive |  |
| 1-3 |  | AGND | Analog GND |  |
| 1-4 |  | AI1 | Channel 1 analog input |  |
| 1-5 |  | AI2 | Channel 2 analog input |  |
| 1-6 |  | V1+ | Channel 1 controllable power output positive |  |
| 1-7 |  | AGND | Analog GND |  |
| 1-8 |  | AI3 | Channel 3 analog input |  |
| 2-1 | Digital input | DI0 | Channel 0 digital input | Optical isolation Logic 0: wet contact 0-3V DC, or dry contact is connected Logic 1: wet contact 5-30V DC, or dry contact is disconnected |
| 2-2 |  | DGND | Digital GND |  |
| 2-3 |  | DI1 | Channel 1 digital input |  |
| 2-4 |  | DI2 | Channel 2 digital input |  |
| 2-5 |  | DGND | Digital GND |  |
| 2-6 |  | DI3 | Channel 3 digital input |  |
| 2-7 | Rainfall | GND | Udometer GND | Udometer interface |
| 2-8 |  | Rain | Udometer input |  |
| 3-1 | 232-0 | TX0 | Channel 0 RS232 transmit (RTU transmit) | RS232-0 and RS485-0 cannot be used at the same time |
| 3-2 |  | RX0 | Channel 0 RS232 receiver (RTU receiver) |  |
| 3-3 |  | GND | Channel 0 RS232 GND |  |
| 3-4 | 485-0 | A0 | Channel 0 RS485 A |  |
| 3-5 |  | B0 | Channel 0 RS485 B |  |
| 3-6 | Vout-2 | V2+ | Channel 2 controllable power output positive | Output voltage is equal to the power supply voltage (default 12V) ,Single rated output current 1A |
| 3-7 |  | V2- | Channel 2 controllable power output negative |  |
| 3-8 | 232-1 | TX1 | Channel 1 RS232 transmit (RTU transmit) | RS232-1 and RS485-1 cannot be used at the same time |
| 3-9 |  | RX1 | Channel 1 RS232 receiver (RTU receiver) |  |
| 3-10 |  | GND | Channel 1 RS232 GND |  |
| 3-11 | 485-1 | A1 | Channel 1 RS485 A |  |
| 3-12 |  | B1 | Channel 1 RS485 B |  |
| 4-1 | 485-2 | A2 | Channel 2 RS485 A | Output voltage is equal to the power supply voltage (default 12V) ,Single rated output current 1A |
| 4-2 |  | B2 | Channel 2 RS485 B |  |
| 4-3 | Vout-3 | V3+ | Channel 3 controllable power output positive | Output voltage is equal to the power supply voltage (default 12V) ,Single rated output current 1A |
| 4-4 |  | V3- | Channel 3 controllable power output negative |  |
| 4-5 | 485-3 | A3 | Channel 3 RS485 A | RS485-3 and Debug Serial cannot be used at the same time through Debug toggle switch |
| 4-6 |  | B3 | Channel 3 RS485 B |  |
| 4-7 | Relay Output | K0+ | Channel 0 relay positive | Maximum switching voltage: 30V DC/250V AC Maximum switching current: 5A Maximum switching power: 150W/1200VA |
| 4-8 |  | K0- | Channel 0 relay negative |  |
| 4-9 |  | K1+ | Channel 1 relay positive |  |
| 4-10 |  | K1- | Channel 1 relay negative |  |
| 4-11 | Digital Output | DO | Digital output | Optical isolation, OC gate output Rated driving current: 50mA Rated driving voltage: 35V |
| 4-12 |  | DOGND | Digital output GND |  |

Installation and Cable Connection

Dimension (The fixing piece is detachable): (Unit: mm)

Installation of antenna:

Installation of antenna:

Cellular antenna (Standard)                      GPS /Beidou antenna (Optional)

The Cellular antenna interface is an SMA female ,labeled "ANT" (5G models have two antennas, namely "ANT1" and "ANT2").Screw the SMA male head of the cellular antenna to the antenna interface, and make sure to screw it tightly so as not to affect the signal quality.

The GPS antenna is SMA female, labeled "GPS/BD". Screw the SMA male of the matching GPS antenna onto the antenna interface ,and make sure to screw it tightly so as not to affect the signal quality.

Installation of SIM/UIM card:

Firstly power off RTU, and press the out button of the SIM/UIM card outlet with a needle object. Then the SIM/UIM card sheath will flick out at once. Put SIM/UIM card into the card sheath (Pay attention to put the side which has metal point outside), and insert card sheath back to the SIM/UIM card outlet.

Installation of cable:

RTU uses the industrial terminal interface. It is recommended to use 22-16 AWG cables for power supply and 28-18 AWG cables for communication.

| RS232 cable (standard) | Debug serial cable (optional） |
| --- | --- |
| Power adapter (optional) | RJ45 network cable (optional) |
| RS485 cable (optional) |  |

RS232 cable:

The signal definition of the DB9F serial communication interface is as follows:

| Color of wire | DB9 female |
| --- | --- |
| Blue(TX) | 2 |
| Brown(RX) | 3 |
| Black(GND) | 5 |

Debug Serial Cable：

It adopts standard DB9 female, and the interface definition is as follows:

| DB9 female | Definition | Remark |
| --- | --- | --- |
| 2 | TXD | RTU data Transmit |
| 3 | RXD | RTU data Receive |
| 5 | RGND | RS232 GND |

Debug serial port and RS485-3 multiplex the same serial port, the debug toggle switch needs to be turned to the ON position for Debug serial to function properly.

Power adapter:

The definition of the 2pin industrial terminal (3.81mm pitch) is as follows:

| Number | Definition | Remark |
| --- | --- | --- |
| 1 | V+ | Main Power positive |
| 2 | V- | Main Power negative |

Network cable:

Insert one end of the network cable direct connection into RTU  Ethernet interface ,and insert the other end into the Ethernet interface of user’s device. The signal connection of network direct cable is as follows:

| RJ45-1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RJ45-2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

RS485 cable:

The signal definition of the RS485 serial communication interface is as follows:

| Color of wire | Definition |
| --- | --- |
| Red | RS485 A |
| Black | RS485 B |

Digital input:

Dry contact, logic 0: connected, logic 1: disconnected

Wet contact, logic 0: 0-3V DC, logic 1: 5-30V DC)

Digital output wiring: optical isolation, OC gate output, 50mA rated driving current, 35V rate driving voltage

Relay: (Maximum switching voltage: 30V DC/250V AC, Maximum switching current: 5A, Maximum switching power: 150W/1200VA)

Analog input: (12-bit ADC, Input current range: 4-20mA, input voltage range: 0-5V)

Udometer:

Controllable power output: (The output voltage is equal to the power supply voltage. The default value is 12V . Single rated output current 1A, total rated output current 2A, built-in overcurrent protection)

Power Supply

Power Adapter (optional)

The power range of the edge computing gateway is DC 9~35V,and the supply must ensure the stability of the power supply (ripple less than 300mV, and ensure the instantaneous voltage does not exceed 35V), and ensure the power supply is greater than 9W.

Warning: When we use other power supply, we should make sure that the rated power is greater than 9W.

We recommend user to use the optional DC 12V/1A power.

Indicator Lights Introduction

Indicator status description:

| LED | Status | Description |
| --- | --- | --- |
| Power (Red) | OFF | Device is powered off or in sleep(static duty)/deep-sleep mode |
|  | ON | Device is powered on |
| SIM (Blue) | OFF | SIM/UIM card not recognized |
|  | ON | SIM/UIM card recognized |
| Online (Green) | OFF | Device is not online |
|  | ON | Device is online |
| RUN (Yellow) | OFF | Device does not work or in deep-sleep mode |
|  | Blink | Device works normally |
|  | ON | Device does not work |
| APP (Reserved) | OFF | TBD |
|  | ON | TBD |
| LINK (Reserved) | OFF | TBD |
|  | ON | TBD |

Wake Up Button Description

RTU has a tact switch ("WAKE"). After enter sleep(static duty) state, press the wake-up button once can wake the device up. In addition, under normal working conditions:

| Button operation | function | Remark |
| --- | --- | --- |
| Press once | Data collection | based on user configuration |
| Press 2 to 3 seconds | Data collection and upload | based on user configuration |
| Press more than 5 seconds | Enter sleep(static duty) mode | Working current< 2mA@12VDC |

Installation Instruction

The enclosure supports mounting lug and 35mm DIN rail.

Lightning protection Introduction

When the RTU device is connected to an outdoor sensor (such as a rain gauge, water level meter, etc.), it is recommended to take appropriate lightning protection measures (such as installing a lightning arrester, etc.) to improve the safety protection level of the equipment.

If you have any questions about the use of the lightning arrester, please consult the technical support engineer of Alotcer!